## Instructions
RCM FMEA Template Pack
Welcome to the Reliability HQ FMEA Template Pack. This workbook follows SAE JA1011 and Moubray's RCM II methodology.
SHEETS IN THIS WORKBOOK:
1. FMEA Worksheet - Main analysis sheet for documenting failure modes and effects
2. Function List - Define equipment functions with performance standards
3. Failure Mode Library - Reference library of common failure modes by equipment type
HOW TO USE:
Step 1: Define the asset boundary and operating context
Step 2: List all functions in the Function List sheet
Step 3: For each function, identify functional failures and failure modes
Step 4: Document failure effects and consequences in the FMEA Worksheet
Step 5: Use the RCM Decision Diagram to select appropriate tasks
COLUMN DEFINITIONS:
Function: What the equipment is expected to do (include performance standard)
Functional Failure: How the function can fail to be fulfilled
Failure Mode: The specific mechanism or cause of the functional failure
Failure Effect: What happens when the failure mode occurs (local and system)
Consequence: Safety (S), Environmental (E), Operational (O), or Non-operational (N)
Current Controls: Existing maintenance or operational tasks
Recommended Task: Proactive task from RCM decision logic
Task Interval: Frequency or condition for task execution
Responsibility: Role or department responsible for task execution
TIPS:
• Be specific about performance standards (e.g., 'pump at 500 L/min' not just 'pump water')
• Each function should have at least one functional failure
• Each functional failure should have at least one failure mode
• Use the Failure Mode Library for common examples and inspiration
• Involve operators, maintainers, and engineers in the analysis
REFERENCE STANDARDS:
• SAE JA1011 - Evaluation Criteria for RCM Processes
• SAE JA1012 - A Guide to the RCM Standard
• Moubray, J. (1997) Reliability-centred Maintenance (RCM II)
© 2026 Reliability HQ ¦ reliabilityhq.com

## FMEA Worksheet
Ref | Asset/System | Function | Functional Failure | Failure Mode | Failure Effect | Consequence | Current Controls | Recommended Task | Task Type | Interval | Responsibility | Notes
1.1 | Cooling Water Pump P-101 | Transfer cooling water from sump to heat exchangers at 500 L/min minimum, at 4-6 bar discharge pressure | Unable to pump water | Impeller wear | Gradual reduction in flow rate and discharge pressure. Overheating of downstream equipment within 30 minutes. Production stoppage required. | O | Monthly vibration monitoring | On-Condition Task | CBM | Monthly | Reliability Team | P-F interval ~3 months
1.2 | Cooling Water Pump P-101 | Transfer cooling water from sump to heat exchangers at 500 L/min minimum, at 4-6 bar discharge pressure | Unable to pump water | Mechanical seal failure | Water leak at seal face. Puddle forming under pump. If undetected, bearing damage within 2-4 hours. | O | Operator rounds (visual) | On-Condition Task | CBM | Daily | Operations | Install drip tray with level sensor
1.3 | Cooling Water Pump P-101 | Transfer cooling water from sump to heat exchangers at 500 L/min minimum, at 4-6 bar discharge pressure | Unable to pump water | Motor bearing failure | Increased noise and vibration. If run to failure, motor seizure and unplanned downtime of 8-12 hours. | O | Vibration analysis | On-Condition Task | CBM | Monthly | Reliability Team | Trend overall velocity
1.4 | Cooling Water Pump P-101 | Transfer cooling water from sump to heat exchangers at 500 L/min minimum, at 4-6 bar discharge pressure | Unable to pump water | Coupling failure | Sudden loss of power transmission. Immediate pump stoppage. Requires 4-hour repair. | O | Visual inspection | On-Condition Task | CBM | Quarterly | Maintenance | Check for rubber debris
2.1 | Cooling Water Pump P-101 | Contain pumped fluid (no external leakage) | External leakage exceeds acceptable limits | Casing gasket degradation | Water seeping at flange faces. Environmental/housekeeping issue. Potential slip hazard. | N | Operator rounds | On-Condition Task | CBM | Daily | Operations | Replace gasket at overhaul
3.1 | Cooling Water Pump P-101 | Protect system from overpressure (PSV-101 relieves at 8 bar) | PSV fails to open at setpoint | PSV spring fatigue/corrosion | System overpressure possible. Heat exchanger tube rupture risk. Safety consequence. | S | None | Scheduled Restoration | TBR | 5 years | Instrument Tech | Statutory requirement
© 2026 Reliability HQ ¦ reliabilityhq.com

## Function List
Ref | Asset/System | Function Statement | Performance Standard | Operating Context Notes | Primary/Secondary
1 | Cooling Water Pump P-101 | Transfer cooling water from sump to heat exchangers | 500 L/min minimum flow, 4-6 bar discharge pressure | Continuous operation 24/7. Ambient temp 15-35°C. Water quality: treated, pH 7-8 | Primary
2 | Cooling Water Pump P-101 | Contain pumped fluid | No visible external leakage |  | Primary
3 | Cooling Water Pump P-101 | Protect system from overpressure | PSV-101 relieves at 8 bar, reseats by 7.2 bar | Statutory requirement BS EN ISO 4126 | Secondary
4 | Cooling Water Pump P-101 | Allow isolation for maintenance | Inlet/outlet valves isolate within 30 seconds |  | Secondary
© 2026 Reliability HQ ¦ reliabilityhq.com

## Failure Mode Library
Equipment Type | Component | Failure Mode | Typical Cause | Detection Method | Typical P-F Interval
Centrifugal Pump | Impeller | Wear/Erosion | Abrasive particles, cavitation | Vibration analysis, flow/pressure trending | 1-6 months
Centrifugal Pump | Impeller | Corrosion | Incompatible materials, aggressive fluid | Inspection at overhaul, performance degradation | 6-24 months
Centrifugal Pump | Mechanical Seal | Face wear | Normal wear, contamination, misalignment | Visual (leakage), seal pressure trending | 1-4 weeks
Centrifugal Pump | Mechanical Seal | Elastomer degradation | Chemical attack, temperature cycling | Visual inspection | N/A (sudden)
Centrifugal Pump | Bearings | Fatigue spalling | Normal wear, overload, contamination | Vibration analysis (bearing frequencies) | 1-3 months
Centrifugal Pump | Bearings | Lubrication breakdown | Insufficient lube, wrong grade, contamination | Oil analysis, temperature monitoring | 1-4 weeks
Centrifugal Pump | Coupling | Elastomer degradation | Age, heat, chemical exposure | Visual inspection (debris) | N/A (inspect monthly)
Centrifugal Pump | Baseplate/Foundation | Loosening | Vibration, thermal cycling | Visual inspection, levelling check | N/A
Electric Motor | Stator winding | Insulation breakdown | Age, overheating, contamination, voltage spikes | Insulation resistance testing, partial discharge | Months
Electric Motor | Stator winding | Turn-to-turn short | Contamination, mechanical damage | Motor current signature analysis | Weeks to months
Electric Motor | Rotor | Broken rotor bars | Thermal stress, manufacturing defect | Motor current signature analysis | Months
Electric Motor | Bearings | Fatigue/wear | Normal wear, misalignment, overload | Vibration analysis | 1-3 months
Electric Motor | Bearings | Electrical fluting | VFD-induced shaft currents | Vibration analysis (characteristic frequencies) | 1-6 months
Electric Motor | Cooling fan | Blade damage/loss | Fatigue, impact | Visual inspection, motor temperature | N/A
Control Valve | Packing | Leakage | Wear, hardening, stem damage | Visual inspection | N/A
Control Valve | Seat/Plug | Erosion | Cavitation, flashing, particulates | Control loop performance, valve position trending | Weeks to months
Control Valve | Actuator diaphragm | Rupture | Age, pressure cycling, chemical attack | Position response testing | N/A (sudden)
Control Valve | Positioner | Calibration drift | Vibration, contamination, electronics | Control loop performance | Months
Ball Valve | Seats | Leakage | Wear, contamination, damage from operation | Leakage test (isolation) | N/A
Ball Valve | Stem seal | External leakage | Wear, over-torquing, corrosion | Visual inspection | N/A
Shell & Tube HX | Tubes | Fouling | Scaling, biological growth, particulates | Process parameters (ΔT, ΔP) | Weeks to months
Shell & Tube HX | Tubes | Corrosion | Incompatible materials, galvanic, erosion-corrosion | Tube inspection, eddy current | Months to years
Shell & Tube HX | Tubes | Tube leak | Corrosion, erosion, vibration fatigue | Helium leak test, process contamination | N/A (sudden)
Shell & Tube HX | Gaskets | Leakage | Age, thermal cycling, over/under torque | Visual inspection | N/A
Pressure Transmitter | Sensing element | Drift | Age, process conditions, overpressure events | Calibration check | 6-24 months
Pressure Transmitter | Impulse line | Blockage | Fouling, freezing, product solidification | Process deviation, comparison with redundant | Variable
Temperature Transmitter | RTD/Thermocouple | Drift | Age, contamination, mechanical damage | Calibration check, cross-comparison | 6-24 months
Level Transmitter | Sensing element | Fouling/coating | Process buildup on sensor | Process deviation, inspection | Variable
Reciprocating Compressor | Piston rings | Wear | Normal wear, contamination, improper lubrication | Capacity test, interstage pressures | Months
Reciprocating Compressor | Valves | Leakage/breakage | Fatigue, contamination, liquid carryover | Valve temperature monitoring, capacity test | Weeks to months
Centrifugal Compressor | Seals | Wear/degradation | Normal wear, contamination | Seal gas consumption, process gas leak detection | Weeks to months
Centrifugal Compressor | Bearings | Wear/damage | Overload, misalignment, lube issues | Vibration, bearing temperature | 1-3 months
Gearbox | Gears | Tooth wear | Normal wear, misalignment, overload | Oil analysis (wear metals), vibration (gear mesh) | 1-6 months
Gearbox | Gears | Pitting/spalling | Fatigue, overload | Vibration analysis, oil analysis | 1-6 months
Gearbox | Bearings | Wear/fatigue | Normal wear, contamination, misalignment | Vibration analysis, oil analysis | 1-3 months
Gearbox | Seals | Leakage | Age, wear, shaft damage | Visual inspection | N/A
Gearbox | Oil | Degradation | Age, oxidation, contamination, overheating | Oil analysis (viscosity, TAN, water) | N/A (trend)
© 2026 Reliability HQ ¦ reliabilityhq.com